## Slide 1: Joint Water Commission Water Treatment Plant Virtual Tour

## Slide 3
The JWC is a partnership agency between the cities of Beaverton, Forest Grove, Hillsboro and the Tualatin Valley Water District (TVWD). The City of Hillsboro manages the JWC and its employees.
Joint Water Commission

## Slide 4
Serves about 450,000 customers in Washington County.
Joint Water Commission
Notes: Located near Forest Grove

## Slide 5
Largest conventional water treatment plant (WTP) in Oregon with a peak capacity of 85 million gallons of water per day (MGD).
Joint Water Commission
Notes: What does conventional mean? mixing, flocculation, sedimentation, filtration, and chlorine disinfection
24 hours/day, 365 days a year. That means holidays and weekends

## Slide 6
Tualatin River
Notes: Normally water comes from the Tualatin River

## Slide 7
Hagg Lake & Barney Reservoir
Notes: In the summer we supplement the lower river with water from hagg lake and barney reservoir

## Slide 8
Spring Hill Pumping Plant
Shared with Tualatin Valley Irrigation District
Owned by the Bureau of Reclamation

## Slide 9
Raw Water Pumps
4 Pumps (Brand new)
400 HP/16,000 GPM each
2 Raw Water Pipelines to WTP
36” & 42”

## Slide 10: Rapid Mix
Notes: Raw water enters the Rapid Mix.
Alum and Chlorine (Cl2) are added just prior to the Rapid Mix.
Caustic, Polymer, and Powdered Activated Carbon (PAC) can also be fed into the Rapid Mix when needed.

## Slide 11: Rapid Mix
Alum and chlorine added (Powdered Activated Carbon and Caustic Soda if needed).
Rapid Mix Valve (new).
Rapid Mix Pumps (new).
Flow sent to Sedimentation Basins A-G.

## Slide 12
Rapid Mixing
Alum
Alum
Alum
Alum
Alum
Alum
Rapid Mix Chamber

## Slide 13
Coagulation
Rapid Mix Chamber

## Slide 14: Flocculation Chambers
Notes: Flow travels through one of seven Flocculation Chambers- Sedimentation Basins.
New valve at Rapid Mix helps distribute flow to Flocculation Chambers-Sedimentation Basins.

## Slide 15: Flocculation Chambers

## Slide 16: Sedimentation Basins
Notes: After Flocculation Chambers water travels through the Basins.
Basins D-G have plate settlers to help with settling.

## Slide 17: Sedimentation Basins
Basins A-C
Basins D-G
Plate settlers D-G

## Slide 18: Sedimentation Basins (fall lines)

## Slide 19: Sedimentation Basins (drained)
Basins A-C
Basins D-G

## Slide 20
Flume
Runs at end of the Sedimentation Basins to Filters
Cl2 and Poly are added

## Slide 21
Filters 1-14
14 Filters x 462 sqft x 8.7 GPM/sf (4,019 GPM each filter)
Cl2 is added

## Slide 22
Filters 1-14:
50” Anthracite
6” Sand
Total media depth: 56”
Filter Media
Configuration
Sand
Anthracite
50in.
6in.
Notes: S

## Slide 23
Filters 15-16
2 Filters x 924 sqft x 12 GPM/sf (11,088 GPM each filter)
Cl2 is added

## Slide 24
Filters 15-16:
72” Anthracite
12” Sand
Total media depth: 84”
Filter Media
Configuration
Sand
Anthracite
72in.
12in.
Notes: S

## Slide 25
Filters: Media
Sand
Anthracite

## Slide 26
Pipe Gallery: Filters 1-14

## Slide 27
Pipe Gallery: Filters 15-16

## Slide 28: Filters to Clearwell
Notes: From the Filters, the water enters the Clearwell where more Cl2 is added along with Caustic for pH control. 1.2 Mgal of water
Clearwell = 1.2 Mgal

## Slide 29
Clearwell
1.3 MG
Caustic Soda is added
Cl2 is added
Holds 1.3 million gallons of water

## Slide 30
Clearwell

## Slide 31: Finished Water Pump Stations
Notes: From the Clearwell, the water is pumped out of the pump stations where Cl2 is added again.
Pump Station #1: 6 pumps = 32,000 GPM
Pump Station #2: 3 pumps = 27,000 GPM

## Slide 32
Finished Water Pump Station #1
Finished Water Pumps 1-6:
3 x 4,000 GPM
2 x 7,000 GPM
1 x 6,000 GPM
Cl2 is added

## Slide 33
Finished Water Pump Station #2
Finished Water Pumps 7-9:
9,000 GPM each
Cl2 is added

## Slide 34: Water Pumped from WTP to:
24” Forest Grove-Dilley Transmission Line
72” North Transmission Line (NTL)
45” South Transmission Line (STL)
Notes: 72” = 6’
Water leaves the treatment plant via the Forest Grove-Dilley transmission line into Forest Grove, via the North transition line that runs up to north Hillsboro and into Tualatin Valley Water District, and via the South Transition line from the Fern Hill Reservoirs into South Hillsboro and Beaverton.

## Slide 35: Fern Hill Reservoirs
2 Reservoirs 20 MG each

## Slide 36: Recycled Water
Sludge from basins is sent out to one of the 5 Sludge Drying Beds (SDBs) via Solids Diversion Pump Station.
Backwash and Filter to Waste water also sent to SDBs via Surge Basins.
Water sent back from Decant Pump Station to RW pipeline to reenter treatment process.
Sludge gets hauled off after drying.

## Slide 37
Sludge Removal

## Slide 38
Surge Basins

## Slide 39
Chemicals used in the Treatment Process

## Slide 40
Chlorine
Chlorine (Cl2) is added for two reasons:
-To disinfect the water
-Maintain water safety all the way to the tap
Chlorine delivered once a week in the summer, and every two weeks in the winter (three 1 ton cylinders per load).

## Slide 41
Aluminum Sulfate
Aluminum Sulfate (Alum) is used as coagulant to form flocculent
Alum delivered about once a week (2 truck loads per order).

## Slide 42
Sodium Hydroxide
Sodium Hydroxide (Caustic Soda/NaOH) is added to raise the pH in order to prevent corrosion. Also used to raise pH in Rapid Mix during storm events.
Sodium Hydroxide is delivered about once a week in the summer, and every two weeks in the winter.

## Slide 43
Filter Aid Polymer
Filter Aid Polymer (Poly) added to assist filters (FAP/Filter Aid Polymer)
Filter Aid Polymer delivered about every six months (18 bags per order).

## Slide 44: Powdered Activated Carbon
Powder Activated Carbon (PAC) is used for Taste and Odors and algal toxins if required.
Powder Activated Carbon “super sacks” delivered via flat bed and stored mostly off-site.

## Slide 45
Backup Power Facility
Backup Generators Online
2 x 2.5 MW Generators
Runs WTP at 37.5 MGD
PGE DSG (Dispatchable Standby Generation) Program
15,000-gallon diesel fuel tank
Enough fuel for 48 hours at full capacity

## Slide 46: Operations
8 Operators (levels 1-4)
12 Hour shifts
7 days on 7 days off
Day and Night shift

## Slide 47: Laboratory

## Slide 48: 1976
20 MGD
4 Filters
2 Sedimentation Basins (A-B)
1 FW Pump Station
And lots of Filbert trees!

## Slide 49: 2023
85 MGD
16 Filters
7 Sedimentation Basins (A-G)
2 FW Pump Stations
No more Filbert trees!